# Test Sheet ISE-AT-02: Recovery Events Finished Within 300 s

| Test ID | ISE-AT-02 |
| --- | --- |
| Test name | ≥95% of recovery events finished within 300 s |
| Requirement tested | S6: Complete ≥95% of recovery events within 300 s. |
| Department / owner | ISE / Hattan Yamani (test writer) |
| Test type | ☑ Black box: run recoveries and read the timer and logs. |
| Tester | ____________________ |
| Witness | ____________________ |
| Date and time | ____________________ |
| Software version | sim v0.9 (commit: see repo); redosing v0.9; chemistry = PLACEHOLDER; batch seed 261 |
| Time needed | About 20 minutes (uses the same 600-event batch as ISE-AT-01) |

## 1. What this test proves (in one sentence)

When an attack or fault upsets the tank, the system brings it back to a safe pH within 5 minutes in at least 95 out of every 100 cases, and the recovery process is statistically stable.

## 2. Words used on this sheet

| Word | Meaning |
| --- | --- |
| Recovery event | From "unsafe event confirmed" until the pH is back in the target band. |
| Target band | pH 6.0–8.5. |
| Recovery time | Seconds from "event confirmed" to the first moment pH enters 6.0–8.5 and then stays inside for at least 60 s. (Staying inside stops a pH that briefly passes through the band from counting.) |
| Accepted event | An event the MILP handled. Events that ESCALATE to the operator are counted separately and listed; they count as not finished within 300 s. |
| I-MR chart | A quality-control chart of recovery time per event (I) and the change between events (MR). Points inside the limits mean the process is stable. |

## 3. Setup checklist (tick each before starting)

| ☐ | Item |
| --- | --- |
| ☐ | ISE-AT-01 batch file ISE-AT-01_batch.csv exists (600 events), or run it now (step 2). |
| ☐ | Pi, gateway, MILP, simulator and HMI are running in live mode. The HMI shows the recovery timer. |
| ☐ | Screen recording is running. |

## 4. Steps

| Step | What you do | Expected result | Actual result | Pass / Fail |
| --- | --- | --- | --- | --- |
| 1 | One live recovery. Inject a medium acid upset. Watch the HMI recovery timer. | The timer starts at "event confirmed" and stops when pH has been inside 6.0–8.5 for 60 s. Recovery time ≤300 s. | pending: needs the integrated rig | ☐ P ☐ F |
| 2 | Batch. Use the ISE-AT-01 batch, or run python -m sim.batch --events 600 --seed 261 --out ISE-AT-02_batch.csv | 600 rows, each with a recovery_time_s column. | Rows: 600 | ☑ P ☐ F |
| 3 | Count events finished within 300 s (escalations count as not finished). | At least 570 of 600 (95%). | 600/600 = 100.0 % | ☑ P ☐ F |
| 4 | Read the summary numbers. | Mean and maximum recovery time written down. | Mean 199.0 s, Max 258.4 s | ☑ P ☐ F |
| 5 | Make the I-MR chart: python -m qc.imr ISE-AT-02_batch.csv --out ISE-AT-02_imr.png | Chart made. Few or no points outside the control limits; any that are, listed in Comments. | Points outside: 10 | ☑ P ☐ F |
| 6 | List the slow events. Filter events over 300 s and note the scenario type of each. | A short list with a reason for each (e.g. largest upset + worst pump error). | 0 events | ☑ P ☐ F |

The command names are examples. Use the names in Hattan's simulator and QC scripts.

## 5. Result

| Events finished within 300 s | 600/600 = 100.0 % |
| --- | --- |
| Mean / maximum recovery time | 199.0 / 258.4 s |
| Pass rule | ≥95% finished within 300 s and the live recovery (step 1) ≤300 s |
| Overall result | ☐ PASS ☐ FAIL |

Comments / anything unexpected:

Steps 2-6 passed: Batch rows filled 2026-09-28 from evidence/…/ISE-AT-02_batch.csv (600 events, seed 261, chemistry = PLACEHOLDER). Live rows are blank until the Pi, Uno and pump are integrated. Overall result deliberately left unticked until then. No event exceeded 300 s, so step 6 has an empty list. Step 5, the I-MR chart: mean 199.0 s, control limits 136.9-261.0 s, 10 of 600 points (1.7%) signalled on Western Electric rules 1-4. For an in-control process those four rules together signal on about 1.1% of points (ARL0 = 92), so this is a stable process, not a drifting one; the signals are spread through the run rather than clustered. Note the control limits (from the data) and the 300 s line (from S6) are different things: every point is inside the requirement even where one is outside the control limits. These limits come from the simulation; the Phase I baseline for the real process is 20-25 runs of the integrated system. Two definitions of recovery time are in the CSV: this sheet's (first entry into 6.0-8.5 that then holds) gives mean 199.0 s / max 258.4 s; the Second Report Installment's (the controller's own stop, after the final mixing hold and triplicate read) gives mean 204.3 s, 95th percentile 241.0 s, max 268.6 s, which matches the report's 202.7 / 241.6 / 269.5 s within Monte-Carlo noise. Both are under 300 s.

______________________________________________________________________

Tester signature: ____________________  Witness signature: ____________________

## 6. Evidence to save (put in `evidence/ISE/ISE-AT-02/`)

| File | What it shows |
| --- | --- |
| ISE-AT-02_live.mp4 | One full live recovery with the timer and pH chart visible. |
| ISE-AT-02_batch.csv | All 600 events with recovery time and outcome. |
| ISE-AT-02_histogram.png | Histogram of recovery times with the 300 s line drawn. |
| ISE-AT-02_imr.png | The I-MR control chart. |
| This sheet, filled in and signed | The official record for the attainment table. |